Experiment 7: synchronous motor characteristics

OBJECT :

- To observe how a synchronous motor can act as a variable inductance or capacitance.

- To obtain the dc current vs ac current characteristics curve for the synchronous motor.

- To determine the full load characteristics of the synchronous motor.

- To determine the pull-out torque of the synchronous motor.

DISCUSSION :

You have learned that positive reactive power is needed to create the magnetic field in an alternating current motor. This reactive power has the disadvantage of producing a low power factor. Low power factors are undesirable for several reasons. Generators, transformers and supply circuits are limited in ratings by their current carrying capacities. This means that the kilowatt load that they can deliver is directly proportional to the power factor of the loads that they supply. For example, a system can deliver only 70 percent of kilowatt load at 0.7 power factor that it can deliver at unity power factor.

The synchronous motor requires considerable reactive power when it operates at no load without any dc excitation to the rotor. It acts like a three-phase inductance load on the power line. When the rotor is excited, it will produce some of the magnetism in the motor with the result that the stator has to supply less, and the reactive power drawn from the power line decreases. If the rotor is excited until it produces all the magnetism, the power line will only have to supply real power to the stator, and the power factor will be unity. As far as the power line is concerned, the synchronous motor now looks like a three-phase resistance load.

If the rotor is excited still further, tending to create more magnetism than the motor needs, then the power line starts supplying negative reactive power to the stator in its attempt to keep the total flux constant. But the negative reactive power corresponds to a capacitor, and the synchronous motor now looks like a three-phase capacitance load to the power line.

At no load, the synchronous motor has the property of acting like a variable inductor/variable capacitor, the value of reactance ( XL or XC) being determined by the amount of dc current flowing in the rotor.

A synchronous motor when used on the same power system with induction motors improves the overall system power factor.

INSTRUMENTS AND COMPONENTS :

Synchronous Motor/Generator Module                                                 EMS  8241

Three-Phase Wattmeter Module                                                            EMS  8441

Electrodynamometer Module                                                                 EMS 8911

# Power Supply Module (120/208 V 3(, 120 Vdc )                                 EMS  8821

AC Metering Module (250 V)                                                               EMS  8426

AC Metering Module (0.5/2.5A)                                                           EMS  8425

DC Metering Module (0.5/2.5A)                                                           EMS  8412

Connection Leads                                                                                   EMS  8941

Timing Belt                                                                                            EMS 8942

PROCEDURE :

Caution: High voltages are present in this Laboratory Experiment! Do not make any connections with the power on! The power should be turned off after completing each individual measurement!

- a) Using your EMS Synchronous Motor/Generator, Wattmeter, Power Supply and Metering Modules, connect the circuit shown in Fig.9-1. Note that the stator windings are connected, through the wattmeter, to the fixed 208 V 3(, output of the power supply, terminals 1, 2 & 3. The voltage adjust control knob should be at zero.

b) If the motor is equipped with switch S, open it at this time.

c) Set the field rheostat for zero resistance (knob turned fully cw)

- a) Turn on the power supply; the motor should be running. Note the value of ac current I1.The motor is drawing positive reactive power from the power supply at zero dc excitation and looks like an inductor.

b) If the motor is equipped with switch S, close it at this time.

c) Gradually increase the dc excitation until the ac current I1 is at its minimum value. Both wattmeters should have equal positive indications, and, as far as the power supply is concerned, the motor looks like a resistor.

d) Note I1, I2, W1, and W2.

e) Increase the dc excitation and note that the ac current I1 begins to increase again. The motor is drawing negative reactive power from the power supply and looks like a capacitor.

- a) With the dc excitation at zero, measure and record E1, I1, W1, and W2 in Table 9-1.

Fig. 9-1.

TABLE  9-1.

| I2 (amps) | E1 (volts) | I1 (amps) | POWER (V A) | W1 ( watts ) | W2 ( watts ) | POWER (WATTS) | PF (COS() |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0 |  |  |  |  |  |  |  |
| 0.1 |  |  |  |  |  |  |  |
| 0.2 |  |  |  |  |  |  |  |
| 0.3 |  |  |  |  |  |  |  |
| 0.4 |  |  |  |  |  |  |  |
| 0.5 |  |  |  |  |  |  |  |
| 0.6 |  |  |  |  |  |  |  |
| 0.7 |  |  |  |  |  |  |  |
| 0.8 |  |  |  |  |  |  |  |
| 0.9 |  |  |  |  |  |  |  |

b) Repeat for each of the dc current values listed in Table 9-1. Take your measurements as quickly as possible when the excitation exceeds 0.6 Adc. Turn off the power supply and change ammeter ranges when the currents drop below 0.5 Adc. Remember to note the polarity of the wattmeter indications.

c) Return the voltage to zero and turn off the power supply.

- Complete Table 9-1 by calculating the apparent power (remember to multiply by 1.73) real power

and power factor for each of the dc currents listed.

- a) From the results of Table 9-1, calculate the reactive power at zero dc rotor current.

b) Is the power factor leading or lagging?

c) From the results of Table 9-1, calculate the reactive power at maximum dc rotor current.

d) Is the power factor leading or lagging?

e) From the results of Table 9-1, calculate the reactive power at minimal stator current.

- a) Using your EMS Synchronous Motor/Generator, Wattmeter, Electrodynamometer, Power Supply and Metering Modules, connect the circuit shown in Fig.9-2. Note that the stator windings are connected to variable three-phase output of the power supply, terminals 4,5 and 6 and that the rotor winding is connected to the fixed dc output of the power supply, terminals 8 and N.

Fig. 9-2.

- a) Couple the motor to the electrodynamometer with the timing belt.

b) Set the dynamometer control knob at its full ccw position

c) Set the synchronous motor rheostat at its full ccw position for maximum resistance( if the motor has switch S keep switch S open)

d) Turn on the power supply and quickly adjust E1 to 208 Vac indicated by the voltmeter. The motor should be running.

8.    a)  If the motor has switch S close the switch S

b) Gradually increase the torque to 9 lbf.in while varying the dc excitation until the indications on

both wattmeters are equal. This corresponds to unity power factor. ( I1 should also be at its

minimum value)

c) Measure and record I 1, I 2, E 2 W1 and W2.

9.  Without changing the dc excitation of Procedure 8, gradually increase the loading until the motor

falls out of synchronization. Record the torque required and turn off the power supply.

10. a) Repeat procedures 7 and 8 but this time, increase the dc excitation to 0.8 Adc  while maintaining a

torque of  9 lbf.in.

b) Measure and record I 1, E 2 W1 and W2

c) Explain why I1 increased in value.

d) Is the power factor leading or lagging?

11.  Determine the pull out torque with 0.8 A dc excitation. Turn off the power supply.

TEST YOUR KNOWLEDGE :

1.    a) Plot the recorded ac currents values vs dc current values from Table 9-1 on the graph.

b) Draw a smooth curve through your plotted points.

c) Plot the recorded ac power factors vs dc current values from Table 9-1 on the graph.

d) Draw a smooth curve through your plotted points.

e) Comment on the appearance of both curves

2.  A synchronous motor is sometimes called a synchronous capacitor. Explain

3.  Might a synchronous motor equally well be called a synchronous inductor?

4.  The pull out torque is affected by the degree of dc excitation. Explain